Safety Venting

**Model SRP-B Fusible Link 08/23/2024**

Suggested Specifications | Section 08 95 16

* 1. Summary

1. Furnish all smoke relief panels, frames, and attachment hardware necessary to complete the work as indicated on the drawings, and as described in the specification.

1.02 Related Sections

1. Steel Framing
2. Flashing and Sheet metal Section
3. Sealants Section

11.03 References

1. American Society for Testing and Materials (ASTM)
2. The Aluminum Association (AA)
3. American Architectural Manufacturers Association (AAMA)
4. NFPA 68 Guide for Venting of Deflagrations, 1999 Edition.
5. Factory Mutual Engineering Corporation, 1-44, Damage-Limiting Construction,   
   July 1991.

1.04 Submittals

1. General: Submit the following according to the Condition of Contract and Division 1 Specification Sections.
2. Product data for each type of explosion & pressure relief vent specified, including details of construction relative to materials, dimensions of individual components, profiles, finishes, and light transmission values.
3. Shop drawings showing fabrication and installation of explosion & pressure relief vents, including plans, elevation, sections, and details of components.

1.05 Quality Testing

1. Materials and work shall conform to the latest edition of reference specification specified herein and to all applicable codes and requirements of local authorities having jurisdiction.
2. Explosion release device shall be FM listed and approved.
3. Units shall meet NFPA 68 Design Guidelines for Deflagration Vents.
4. Single Source Responsibility: Obtain explosion & pressure relief vents from one source of a single manufacturer.

1.06 Delivery, Storage, & Handling

1. All explosion & pressure relief vents, frames and curbs shall be factory assembled in units and shipped to the job site.
2. Deliver to site in original, unopened containers and/or pallets bearing manufacturer’s name and label.

1.07 Limited Warranty

1. Manufacturers shall provide limited warranty that the units provided will be free of defects in materials and workmanship for a period of one (1) year from date of substantial completion.

PART 2 PRODUCTS

2.01 Manufacturers

1. Explovent® XRV-TP Basis of Design manufactured by Construction Specialties subject to compliance with requirements listed. The grilles and related materials herein specified and indicated on the drawings shall be manufactured by: Construction Specialties, 3 Werner Way, Lebanon, NJ 08833. Tel: 800.233.8493. Email: [cet@c-sgroup.com](mailto:cet@c-sgroup.com). No substitutions.
2. Installation shall be performed in accordance with approved drawings and installation instructions.
3. Manufacturer shall have complete in-house finishing capabilities.

2.02 Materials

1. Frames shall be constructed of ASTM B 221 alloy 6063-T5 aluminum, mitered and welded with sufficient seepage ports. Mill finished.
2. Fasteners to be corrosion resistant.
3. Curbs shall be constructed with a prefabricated aluminum curb, 3003-H14 alloy sheets. Curbs to be 12" high with mounting flange and shall include manufacturer’s standard double wall aluminum curb with insulation. Mill finished.

2.03 Fabrication

1. Model XRV-TP: Fiberglass Translucent Panel Explosion Relief Vents shall release automatically at an outward pressure of — lb./ft2 (20 psf recommended) using FM approved release devices.
2. Panels shall be 2-3/4" thick and consist of architectural grade glass fiber reinforced polymer faces bonded to an interlocked aluminum I-beam grid core.
3. Tether restraint included eliminating unit from being thrown from immediate area.

PART 3 EXECUTION

3.01 Installation

1. Preparatory work: Standard trade practices are recommended for preparation of structural arrangements for installation of APC vents or skylights.
2. Method: Individual APC units are furnished completely assembled, ready for installation on the roof deck, and for flashing into the roof system. Tandem arrays are delivered in accordance with drawings and instructions provided
3. Installation, flashing, and roofing materials are not included.